## All Devices
Site | DeviceName | DeviceId | DeviceProfile | DeviceType | Vendor | AppVersion | Active | HasSchedule | ScheduleKeys | ScheduleScope | ScheduleFormat | DecodedTimetable (Thu 2026-10-22) | Confidence | Notes
6261 | gk-6261-boilercontrol-1 | 08954210-6f12-11f1-a25c-c7bd0b73b31f | boilerControl | boilerControl-V2 | Lighthouse | 3.3.0 | Yes | Yes | CHZ1.schedule, CHZ2.schedule, DHW.schedule, recirc_pump.schedule, accom_1.schedule, accom_2.schedule | SHARED_SCOPE | boilerControl-json | DHW: 06:00-01:00 (57°C daily); CHZ1: 09:00-23:00 (21°C daily); CHZ2: 09:00-23:00 (21°C daily); Pump: 06:00-01:00 (ON/OFF) | PROVEN | V2 hw2; 2CH+DHW+recirc; accom_1 & accom_2 empty; CHZ optimum_start_stop=true; CHZ schedules last updated 2026-10-16
6261 | gk-6261-salusit700-1 | 4b3882d0-7b79-11f1-a25c-c7bd0b73b31f | salusDevice | salus-IT700 | Salus | — | Yes | No | scheduleEnable (TIMESERIES only) | TIMESERIES | flag-only | N/A — schedule body stored on-device, not in TB | PROVEN | IT700TX thermostat; scheduleEnable value not fetched; gateway offline
6261 | gk-6261-salusit700-gateway-1 | 0b3cf6c0-7b79-11f1-a25c-c7bd0b73b31f | salusDevice | salus-IT700 | Salus | — | No | No | — | N/A | none | N/A | PROVEN | SAWZ600GW gateway; inactive/offline; thermostat operates independently
6261 | gk-6261-ElecAMR-1 | a5025230-529a-11f1-a25c-c7bd0b73b31f | AMR_profile | amr | — | — | Unknown | No | — | N/A | none | N/A | UNRESOLVED | SERVER_SCOPE returned empty array; active status cannot be determined
6261 | gk-6261-GasAMR-1 | cbe54ec0-529a-11f1-a25c-c7bd0b73b31f | AMR_profile | amr | — | — | No | No | — | N/A | none | N/A | PROVEN | siteName='#REF!' in SERVER_SCOPE — provisioning data error; Utility=Gas
6261 | gk-6261-kitchen-r10a | da8c60a0-7ba1-11f1-a25c-c7bd0b73b31f | remoteItProfile | remoteit | — | — | No | No | — | N/A | none | N/A | PROVEN | remoteIt; inactive; remote access unavailable
6261 | gk-6261-maindb-r10a | b2b65c50-7621-11f1-a25c-c7bd0b73b31f | remoteItProfile | remoteit | — | — | No | No | — | N/A | none | N/A | PROVEN | remoteIt; inactive
6261 | gk-6261-bainmarie-1 | 569c0e90-7b64-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer only) | TIMESERIES | none | N/A — raw Tuya device timer, not a TB attribute | PROVEN | Owon; schedule TS key is raw Tuya internal timer, not configurable in TB
6261 | gk-6261-barfans-1 | eff180c0-7abf-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou smart switch; no schedule key
6261 | gk-6261-barfans-2 | d4f675a0-7abf-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou smart switch
6261 | gk-6261-externallighting-1 | 96057650-7b70-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou; no schedule TS key
6261 | gk-6261-grill-1 | 86ada8f0-7b64-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou; no schedule TS key
6261 | gk-6261-merrychef-1 | f5083930-7b6b-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou; no schedule TS key
6261 | gk-6261-merrychef-2 | a58187d0-7b6c-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6261 | gk-6261-merrychef-3 | 9573db20-7b64-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6261 | gk-6261-overdoorheater-1 | 48f58c30-7abf-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou; 1 active alarm at time of read
6261 | gk-6261-overdoorheater-2 | 79d28ce0-7abf-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6261 | gk-6261-overdoorheater-3 | a6f39700-7abf-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6261 | gk-6261-combioven-1 | 4d13dae0-7b6b-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon
6261 | gk-6261-dishwasher-1 | e2aad681-7b6b-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon
6261 | gk-6261-extractfan-1 | 37d8cc50-7b6e-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon
6261 | gk-6261-fryer-1 | c1e312b0-7b6a-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon
6261 | gk-6261-heatedgantry-1 | a6ea1220-7b64-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon
6097 | gk-6097-boilercontrol-1 | 148fd140-5520-11f1-a25c-c7bd0b73b31f | boilerControl | boilerControl-V2 | Lighthouse | 3.3.0 | Yes | Yes | CHZ1.schedule, DHW.schedule, recirc_pump.schedule (CHZ2, accom_1, accom_2 empty) | SHARED_SCOPE | boilerControl-json | DHW: 06:00-23:00 (57°C daily); CHZ1: 11:00-22:00 Thu (21°C) — weekday/weekend split; Pump: 06:00-23:55 daily | PROVEN | V2 hw2; 1CH+DHW; cellular modem; CHZ1 has weekday/weekend split (4-entry); CHZ2 present but empty and not in channels; last CHZ1 update 2026-10-09
6097 | gk-6097-salusit700-1 | 46460eb0-6007-11f1-a25c-c7bd0b73b31f | salusDevice | salus-IT700 | Salus | — | Yes | No | scheduleEnable (TIMESERIES only) | TIMESERIES | flag-only | N/A | PROVEN | IT700TX; salusLocation='axe and cleaver'; gateway offline
6097 | gk-6097-salusit700-gateway-1 | 0264bcf0-6007-11f1-a25c-c7bd0b73b31f | salusDevice | salus-IT700 | Salus | — | No | No | — | N/A | none | N/A | PROVEN | SAWZ600GW-5E10D800 gateway; inactive/offline
6097 | gk-6097-ElecAMR-1 | 58a5d420-529a-11f1-a25c-c7bd0b73b31f | AMR_profile | amr | — | — | No | No | — | N/A | none | N/A | PROVEN | Inactive
6097 | gk-6097-GasAMR-1 | a8537900-529a-11f1-a25c-c7bd0b73b31f | AMR_profile | amr | — | — | No | No | — | N/A | none | N/A | PROVEN | Inactive
6097 | gk-6097-bainmarie-1 | d8b860d0-5ffe-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon
6097 | gk-6097-barfans-1 | 3fa9dd90-5ff1-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6097 | gk-6097-coffeemachine-1 | 81514710-6000-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6097 | gk-6097-combioven-2 | 0a4b7c01-6008-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon
6097 | gk-6097-dishwasher-1 | b35716b0-6008-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon
6097 | gk-6097-externallighting-1 | c9d2f9c0-5ff1-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6097 | gk-6097-extractfan-1 | 37c5ea60-6000-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou (no schedule TS key — differs from 6261 owon extractfan)
6097 | gk-6097-fryer-1 | 9e16ca40-6006-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon
6097 | gk-6097-fryer-2 | 3985acb0-6009-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon
6097 | gk-6097-glasswasher-1 | b98feb90-5ff1-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6097 | gk-6097-grill-1 | e69ae8c0-6009-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6097 | gk-6097-hcuboard-1 | 4e253830-5ffe-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6097 | gk-6097-heatedgantry-1 | 2e5db0e1-5ffe-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-owon | Tuya | — | Yes | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon
6097 | gk-6097-merrychef-1 | 3322e3a0-600a-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6097 | gk-6097-merrychef-2 | 390abae0-600a-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Tongou
6769 | gk-6769-boilercontrol-1 | 0a4ceb80-8e26-11f0-af01-0f88a04b9252 | boilerControl | boilerControl-V1 | Lighthouse | 2.8.2 | Yes | Yes | output2Schedule, output3Schedule, output4Schedule | CLIENT_SCOPE + SHARED_SCOPE | boilerControl-json | CH2: 11:00-21:30 daily (21°C); CH3: 11:00-21:30 daily (21°C); DHW: 10:30-23:00 Mon-Fri / 23:55 Sat-Sun (60°C) | PROVEN | V1 hw; output1OutputMask CLIENT=[false,true,true,false] but SHARED=[false,true,true,true] → DHW enabled (DEDUCED from embedded outputs[]); 3 LoRaWAN temp sensors; no active overrides
6769 | gk-6769-salusit700-1 | fa7a73a0-b59c-11f0-bb17-9fd297bb4ff9 | salusDevice | salus-IT700 | Salus | — | Yes | No | scheduleEnable (TIMESERIES only) | TIMESERIES | flag-only | N/A | PROVEN | IT700TX; gateway offline
6769 | gk-6769-salusit700-gateway-1 | b9d5a730-be0b-11f0-bb17-9fd297bb4ff9 | salusDevice | salus-IT700 | Salus | — | No | No | — | N/A | none | N/A | PROVEN | SAWZ600GW-5E0B6B98 gateway; inactive
6769 | gk-6769-ElecAMR-1 | 3882df00-cec... | AMR_profile | amr | — | — | No | No | — | N/A | none | N/A | PROVEN | Inactive
6769 | gk-6769-GasAMR-1 | 371433d1-cec... | AMR_profile | amr | — | — | No | No | — | N/A | none | N/A | PROVEN | Inactive
6769 | gk-6769-lwgateway | 04cc47a0-84bc-11f0-af01-0f88a04b9252 | remoteItProfile | lorawan-gateway | — | — | No | No | — | N/A | none | N/A | PROVEN | LoRaWAN gateway for Watteco temp sensors; remoteItActive=true at site (different device); active=false at time of sweep
6769 | gk-6769-maindb-r10a | a600cfc0-a42d-11f0-aef9-63eb6f282fc9 | R10A Modbus Gateway | remoteit | — | — | Yes | No | — | N/A | none | N/A | PROVEN | R10A Modbus gateway
6769 | Device 70B3D5E75F20068E | 31bc2d50-b97a-11f0-bb17-9fd297bb4ff9 | boiler-control | lorawan-sensor | Watteco | fw 3.5.2 | Yes | No | — | N/A | none | N/A | PROVEN | Clim'o temp sensor; label=gk-6769-tempsensor-1; linked-output-num=3; use decoded JSON for actual temp
6769 | Device 70B3D5E75F2004DF | 5664a330-b97a-11f0-bb17-9fd297bb4ff9 | boiler-control | lorawan-sensor | Watteco | fw 3.5.2 | Yes | No | — | N/A | none | N/A | UNRESOLVED | Clim'o temp sensor; label=gk-6769-tempsensor-2; linked-output-num UNRESOLVED (sweep token limit)
6769 | Device 70B3D5E75F2004C1 | 0f012f90-b97a-11f0-bb17-9fd297bb4ff9 | boiler-control | lorawan-sensor | Watteco | fw 3.5.2 | Yes | No | — | N/A | none | N/A | PROVEN | Clim'o temp sensor; label=gk-6769-tempsensor-3; linked-output-num=2; temp 19.3°C
6769 | gk-6769-dishwasher-1 | bdff92e0-aa6... | tuya Profile | tuya-tongou | Tuya | — | Yes | Partial | scheduleHEX (SERVER_SCOPE) | SERVER_SCOPE | hex-string | UNRESOLVED format — hex binary, not yet decoded | PROVEN | scheduleHEX owon/hex-string format; Tuya-specific spec needed
6769 | gk-6769-cellar-1 | 173f7570-bfc... | tuya Profile | tuya-tongou | Tuya | — | No | No | — | N/A | none | N/A | PROVEN | Inactive
6769 | gk-6769-various-tuya | (various) | tuya Profile | tuya-tongou | Tuya | — | Yes/No | No | — | N/A | none | N/A | PROVEN | 34 devices total at site including cellardb, pubdb, kitchendb, externalheating x2, externallighting x2, glasswasher x2, etc.
4331 | gk-4331-boilercontrol-1 | (ID from B) | boilerControl | boilerControl-V1 | Lighthouse | 2.8.2 | Yes | Yes | output2Schedule, output3Schedule, output4Schedule | CLIENT_SCOPE + SHARED_SCOPE | boilerControl-json | CH2/3: Sched 11:00-12:00 + 17:00-18:30 (21°C) BUT override=1 (forced ON); DHW: 10:30-23:00 Thu (50°C) | PROVEN | V1; output2Override=output3Override=1 (CH zones manually overridden ON at time of sweep); DHW normal; CLIENT top-level outputXSchedule stale vs outputs[] embedded (DEDUCED)
4331 | gk-4331-salusit700-1 | 0390a770-b59d-11f0-bb17-9fd297bb4ff9 | salusDevice | salus-IT700 | Salus | — | No | No | scheduleEnable (TIMESERIES only) | TIMESERIES | flag-only | N/A | PROVEN | IT700TX; active=false (inactive); gateway also inactive
4331 | gk-4331-salusit700-gateway-1 | c748a570-be0b-11f0-bb17-9fd297bb4ff9 | salusDevice | salus-IT700 | Salus | — | No | No | — | N/A | none | N/A | PROVEN | SAWZ600GW gateway; inactive
4331 | gk-4331-lwgateway | 8b6bffc0-83dc-11f0-af01-0f88a04b9252 | remoteItProfile | lorawan-gateway | — | — | No | No | — | N/A | none | N/A | PROVEN | LoRaWAN gateway; active=false; alarm: Remote.IT Gateway Offline
4331 | gk-4331-supplyfan-1 | 0b047720-9a18-11f0-aef9-63eb6f282fc9 | tuya Profile | tuya-tongou | Tuya | — | Yes | Partial | scheduleHEX (SERVER_SCOPE comma-delimited) | SERVER_SCOPE | hex-string | Thu: ON 11:00 (all days), OFF 21:30 (Tue-Sun Thu✓), OFF 20:30 Mon only | PROVEN | scheduleHEX comma-delimited tongou format; 3 active alarms including critical
4331 | gk-4331-externallighting-1 | 1176b510-9a0d-11f0-aef9-63eb6f282fc9 | tuya Profile | tuya-tongou | Tuya | — | Yes | Partial | scheduleHEX (SERVER_SCOPE comma-delimited) | SERVER_SCOPE | hex-string | ON 16:00 daily, OFF 00:00 daily, OFF 23:30 Mon only | PROVEN | scheduleHEX comma-delimited tongou format; 2 critical alarms
4331 | gk-4331-glasswasher-1 | 6d02fc90-9a0d-11f0-aef9-63eb6f282fc9 | tuya Profile | tuya-tongou | Tuya | — | Yes | Partial | scheduleHEX (SERVER_SCOPE comma-delimited) | SERVER_SCOPE | hex-string | ON 10:30 daily, OFF 00:00 daily, OFF 23:30 Mon only | PROVEN | scheduleHEX comma-delimited; asset registered (Fagor AD-505SOFTH)
4331 | gk-4331-merrychef-1 | ca1451e0-9a17-11f0-aef9-63eb6f282fc9 | tuya Profile | tuya-tongou | Tuya | — | Yes | Partial | scheduleHEX (SERVER_SCOPE comma-delimited) | SERVER_SCOPE | hex-string | ON 10:40 daily, OFF 01:00 daily | PROVEN | scheduleHEX comma-delimited; Merrychef Eikon E3 XE
4331 | gk-4331-salgrill-1 | 6d50f480-9a18-11f0-aef9-63eb6f282fc9 | tuya Profile | tuya-owon | Tuya | — | Yes | Partial | scheduleHEX (SERVER_SCOPE hex-string) | SERVER_SCOPE | hex-string | UNRESOLVED — hex binary format, Tuya DPS spec needed | PROVEN | scheduleHEX hex-string owon format; 2 critical alarms; raw: 7F0A1E01017E151E000101141E0001
4331 | gk-4331-extractfan-1 | f5dc97e0-9a19-11f0-aef9-63eb6f282fc9 | tuya Profile | tuya-owon | Tuya | — | Unknown | No | schedule (TIMESERIES raw Tuya timer) | TIMESERIES | none | N/A | PROVEN | Owon; SERVER_SCOPE returned empty (connection error during sweep)
4331 | gk-4331-freezer-1 | defdc230-9a0d-11f0-aef9-63eb6f282fc9 | tuya Profile | tuya-owon | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Owon refrigeration sensor (EUI A84041C2315E5568); alarm: Toggle switch mismatch with schedule state
4331 | gk-4331-fridge-1 | ab0e6680-9a0f-11f0-aef9-63eb6f282fc9 | tuya Profile | tuya-owon | Tuya | — | Yes | No | — | N/A | none | N/A | PROVEN | Owon refrigeration sensor
4331 | gk-4331-maindb-r10a | 6683d150-8fdb-11f0-af01-0f88a04b9252 | R10A Modbus Gateway | remoteit | — | — | No | No | — | N/A | none | N/A | PROVEN | R10A Modbus gateway; active=false; metering_map has 4 circuits
4331 | gk-4331-various-tuya/meter | (various) | tuya/meterOnly | other | Tuya/— | — | Yes/No | No | — | N/A | none | N/A | PROVEN | ~30 devices total at site; roof x3 (refrigeration sensors); DB sub-boards (meterOnly)
5208 | gk-5208-salusit500-f1 | (ID from C) | salusDevice | salus-IT500 | Salus | — | No | Yes | schedule A00-A06 (SERVER_SCOPE) | SERVER_SCOPE | nibble-encoded | UNRESOLVED — proprietary A00-A06 format not decoded | PROVEN | IT500; zone f-1 (floor 1); ALL IT500 at 5208 OFFLINE (active=false); last active ~June 2026
5208 | gk-5208-salusit500-f2 | (ID from C) | salusDevice | salus-IT500 | Salus | — | No | Yes | schedule A00-A06 (SERVER_SCOPE) | SERVER_SCOPE | nibble-encoded | UNRESOLVED — weekday/weekend pattern visible (A05/A06 differ from A00-A04) | PROVEN | IT500; zone f-2; weekday schedule differs from weekend (A05/A06 different values)
5208 | gk-5208-salusit500-f3 | (ID from C) | salusDevice | salus-IT500 | Salus | — | No | Yes | schedule A00-A06 (SERVER_SCOPE) | SERVER_SCOPE | nibble-encoded | UNRESOLVED | PROVEN | IT500; zone f-3; all 7 days identical schedule
5208 | gk-5208-salusit500-r1 | (ID from C) | salusDevice | salus-IT500 | Salus | — | No | Yes | schedule A00-A06 (SERVER_SCOPE) | SERVER_SCOPE | nibble-encoded | UNRESOLVED | PROVEN | IT500; zone r-1 (room 1); all 7 days identical
5208 | gk-5208-salusit500-r2 | (ID from C) | salusDevice | salus-IT500 | Salus | — | No | Yes | schedule A00-A06 (SERVER_SCOPE) | SERVER_SCOPE | nibble-encoded | UNRESOLVED | PROVEN | IT500; zone r-2; all 7 days identical
5208 | gk-5208-salusit500-r3 | (ID from C) | salusDevice | salus-IT500 | Salus | — | No | Yes | schedule A00-A06 (SERVER_SCOPE) | SERVER_SCOPE | nibble-encoded | UNRESOLVED | PROVEN | IT500; zone r-3; all 7 days identical
5208 | gk-5208-exractfan-1 | (ID from C) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | — | N/A | none | N/A | PROVEN | light_mode=relay; simple on/off device
5208 | gk-5208-supplyfan-1 | (ID from C) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | — | N/A | none | N/A | PROVEN | light_mode=relay; simple on/off device
6164 | gk-6164-boilercontrol-1 | (ID from C) | boilerControl | boilerControl-V2 | Lighthouse | ~3.x | Unknown | Yes | CHZ1.schedule, CHZ2.schedule, DHW.schedule, recirc_pump.schedule, accom_1.schedule, accom_2.schedule | CLIENT_SCOPE + SHARED_SCOPE | boilerControl-json | CHZ1 Thu: 10:00-23:00 (21°C Tue-Fri group); DHW Thu: 11:00-22:00 (57°C); see multi-rule schedule | PROVEN | V2 format confirmed; matches schedule.js decoder; Mon+Sat+Sun 09:00 vs Tue-Fri 10:00 on CHZ1
6164 | gk-6164-salusit700-1 | (ID from C) | salusDevice | salus-IT700 | Salus | — | Yes | No | scheduleEnable=2 (TIMESERIES) | TIMESERIES | flag-only | N/A — scheduleEnable=2 = temp hold mode; schedule body on-device only | PROVEN | IT700TX; scheduleEnable=2 (hold); gateway offline; salusLocation=Accomodation stat
6164 | gk-6164-salusit700-gateway-1 | (ID from C) | salusDevice | salus-IT700 | Salus | — | No | No | — | N/A | none | N/A | PROVEN | SAWZ600GW gateway; inactive/offline
6164 | gk-6164-ElecAMR-1 | (ID from C) | AMR_profile | amr | — | — | Unknown | No | — | N/A | none | N/A | PROVEN | No schedule
6164 | gk-6164-GasAMR-1 | (ID from C) | AMR_profile | amr | — | — | Unknown | No | — | N/A | none | N/A | PROVEN | No schedule
6164 | gk-6164-chargrill-1 | 3b643a80-8686-11f1-a25c-c7bd0b73b31f | tuya Profile | tuya-tongou | Tuya | — | Unknown | Yes | schedule (TIMESERIES Base64 binary) | TIMESERIES | base64-binary | Thu (0x1E=Mon+Tue+Wed+Thu): service ON 11:00; OFF 21:30; preheat phases 09:00 + 10:00 | PROVEN | 9-record blob; Day=0x1E covers Thu; action byte 1=service on, 0=preheat phases (DEDUCED)
6164 | gk-6164-combioven-1 | (ID from C) | tuya Profile | tuya-owon | Tuya | — | Unknown | Yes | schedule (TIMESERIES Base64 binary) | TIMESERIES | base64-binary | Thu (0x1E): service ON 10:30; preheat 08:30 + 09:30; OFF varies by day | PROVEN | 9-record blob; complex day-group schedule
6164 | gk-6164-dishwasher-1 | (ID from C) | tuya Profile | tuya-owon | Tuya | — | Unknown | Yes | schedule (TIMESERIES Base64 binary) | TIMESERIES | base64-binary | Thu in 0x18 group: ON 10:30; Sun+Mon+Tue+Wed+Thu off 23:00 | PROVEN | 9-record blob; Thu covered by 0x18 (Wed+Thu) group
6164 | gk-6164-fryer-1 | (ID from C) | tuya Profile | tuya-owon | Tuya | — | Unknown | Yes | schedule (TIMESERIES Base64 binary) | TIMESERIES | base64-binary | Thu (0x1E): service ON 11:15; preheat 09:15 + 10:15; OFF 21:30 | PROVEN | 9-record blob; matches chargrill pattern with 15-min offset
6164 | gk-6164-fryer-2 | (ID from C) | tuya Profile | tuya-owon | Tuya | — | Unknown | Yes | schedule (TIMESERIES Base64 binary) | TIMESERIES | base64-binary | Thu (0x1E + 0x7F): preheat 09:15 + 10:15; service ON 11:15; OFF 21:30 (all days) | PROVEN | 8-record blob
6164 | gk-6164-fryer-3 | (ID from C) | tuya Profile | tuya-owon | Tuya | — | Unknown | Yes | schedule (TIMESERIES Base64 binary) | TIMESERIES | base64-binary | Identical to fryer-2; Thu: preheat 09:15 + 10:15; service ON 11:15; OFF 21:30 | PROVEN | 8-record blob; same Base64 as fryer-2
6164 | gk-6164-grill-1 | (ID from C) | tuya Profile | tuya-tongou | Tuya | — | Unknown | Yes | schedule (TIMESERIES Base64 binary) | TIMESERIES | base64-binary | DEDUCED similar pattern to chargrill; specifics not fully decoded | DEDUCED | Base64 binary blob confirmed; full decode in Agent C data
6164 | gk-6164-heatedgantry-1 | (ID from C) | tuya Profile | tuya-owon | Tuya | — | Unknown | Yes | schedule (TIMESERIES Base64 binary) | TIMESERIES | base64-binary | DEDUCED similar pattern; specifics not fully decoded | DEDUCED | Base64 binary blob confirmed
6164 | gk-6164-pastacooker-1 | (ID from C) | tuya Profile | tuya-owon | Tuya | — | Unknown | Yes | schedule (TIMESERIES Base64 binary) | TIMESERIES | base64-binary | DEDUCED similar pattern; specifics not fully decoded | DEDUCED | Base64 binary blob confirmed
6164 | gk-6164-coffeemachine-1 | (ID from C) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | light_mode=relay | TIMESERIES | none | N/A — simple on/off relay, no schedule | PROVEN | light_mode=relay; no schedule
6164 | gk-6164-dhw-1 | (ID from C) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | light_mode=relay | TIMESERIES | none | N/A — named DHW but operates as simple relay | PROVEN | light_mode=relay; no schedule in TB despite DHW naming
6164 | gk-6164-externallighting-1 | (ID from C) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | light_mode=relay | TIMESERIES | none | N/A | PROVEN | light_mode=relay
6164 | gk-6164-extractfan-1 | (ID from C) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | — | N/A | none | N/A | PROVEN | No schedule
6164 | gk-6164-glasswasher-1 | (ID from C) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | — | N/A | none | N/A | PROVEN | No schedule
6164 | gk-6164-merrychef-1 | (ID from C) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | light_mode=relay | TIMESERIES | none | N/A | PROVEN | light_mode=relay; no schedule
6164 | gk-6164-supplyfan-1 | (ID from C) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | — | N/A | none | N/A | PROVEN | No schedule
6164 | gk-6164-supplyfan-2 | (ID from C) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | — | N/A | none | N/A | PROVEN | No schedule
122 | gk-122-boilercontrol-1 | 94249e20-7a0c-11f1-a25c-c7bd0b73b31f | boilerControl | boilerControl-V2 | Lighthouse/Airedale | 3.3.0 | Yes | Yes | CHZ1.schedule, DHW.schedule, recirc_pump.schedule (CHZ2/accom empty) | SHARED_SCOPE | boilerControl-json | DHW Thu: 11:00-22:00 (57°C, Tue-Fri group); CHZ1 Thu: 10:00-23:00 (21°C, Tue-Fri group); Pump Thu: 11:00-22:00 ON | PROVEN | V2 hw2; 1CH+DHW; complex day-split (Mon+Sat+Sun vs Tue-Fri); Mon unique 22:30 CHZ1 off; LoRaWAN sensors provisioned but lwgateway NOT deployed at site
122 | gk-122-salusit700-1 | 6a317130-868a-11f1-a25c-c7bd0b73b31f | salusDevice | salus-IT700 | Salus | — | Yes | No | scheduleEnable=2 (TIMESERIES) | TIMESERIES | flag-only | N/A — scheduleEnable=2 = hold mode | PROVEN | IT700TX-025E1675; label=Accommodation Stat; gateway offline
122 | gk-122-salusit700-gateway-1 | 2d60bf40-868a-11f1-a25c-c7bd0b73b31f | salusDevice | salus-IT700 | Salus | — | Unknown | No | — | N/A | none | N/A | PROVEN | SAWZ600GW-001E5E10DB38; ZigBee gateway; inactive
122 | gk-122-ElecAMR-1 | 86859a60-529a-11f1-a25c-c7bd0b73b31f | AMR_profile | amr | — | — | Unknown | No | — | N/A | none | N/A | PROVEN | No schedule
122 | gk-122-GasAMR-1 | ad0a4a50-529a-11f1-a25c-c7bd0b73b31f | AMR_profile | amr | — | — | Unknown | No | — | N/A | none | N/A | PROVEN | No schedule
122 | gk-122-fryer-1/2/3 | (various) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | — | N/A | none | N/A | PROVEN | 3 fryers; no schedule visible in TB at site 122
122 | gk-122-combioven-1/2 | (various) | tuya Profile | tuya-owon | Tuya | — | Unknown | No | — | N/A | none | N/A | PROVEN | 2 combi ovens
122 | gk-122-various-tuya | (various) | tuya Profile | tuya-tongou | Tuya | — | Unknown | No | — | N/A | none | N/A | PROVEN | 23 devices total; chargrill, grill x2, glasswasher x2, externalheating x3, externallighting, extractfan, dishwasher, heatedgantry, bainmarie
6770 | gk-6770-boilercontrol-1 | 0a4f8390-8e26-11f0-af01-0f88a04b9252 | boilerControl | boilerControl-V1 | Lighthouse/Airedale | 2.8.2 | Yes | Yes | output2Schedule, output3Schedule (output4 empty) | CLIENT_SCOPE + SHARED_SCOPE | boilerControl-json | CH2: 11:00-12:00 + 17:00-18:30 daily (21°C) — SPLIT lunch+dinner; CH3: identical; DHW: no schedule (empty) | PROVEN | V1; output1OutputMask=[false,true,true,true] = outputs 2/3/4 active; output4Schedule EMPTY despite DHW cylinder (Lockinvar); split-day pattern (lunch+dinner service)
6770 | gk-6770-intesis-688ce553 | 6ce65480-5e68-11f1-a25c-c7bd0b73b31f | default | intesis | Intesis | — | Yes | No | — | N/A | none | N/A | PROVEN | Intesis AC unit; active=true; config in Intesis hardware/cloud, not TB; no schedule in TB
6770 | gk-6770-intesis-6b4a013d | 6ce78d00-5e68-11f1-a25c-c7bd0b73b31f | default | intesis | Intesis | — | Yes | No | — | N/A | none | N/A | PROVEN | Intesis AC unit; active=true
6770 | gk-6770-intesis-ed277306 | 6ce2ab01-5e68-11f1-a25c-c7bd0b73b31f | default | intesis | Intesis | — | No | No | — | N/A | none | N/A | PROVEN | Intesis AC unit; active=false at time of sweep
6770 | gk-6770-salusit700-1 | fac426d0-b59c-11f0-bb17-9fd297bb4ff9 | salusDevice | salus-IT700 | Salus | — | Unknown | No | scheduleEnable (TIMESERIES only) | TIMESERIES | flag-only | N/A | PROVEN | IT700TX-025CECE8
6770 | gk-6770-salusit700-2 | 7cd5f520-b805-11f1-bf95-995fa7662af0 | salusDevice | salus-IT700 | Salus | — | Unknown | No | scheduleEnable (TIMESERIES only) | TIMESERIES | flag-only | N/A | PROVEN | IT700TX-025CFBD6; 2 IT700TX at this site
6770 | gk-6770-salusit700-gateway-1 | ba4f1cf0-be0b-11f0-bb17-9fd297bb4ff9 | salusDevice | salus-IT700 | Salus | — | Unknown | No | — | N/A | none | N/A | PROVEN | SAWZ600GW-5E0B4FD8 gateway
6770 | gk-6770-lwgateway | 43c85320-872f-11f0-af01-0f88a04b9252 | remoteItProfile | lorawan-gateway | — | — | Yes | No | — | N/A | none | N/A | PROVEN | LoRaWAN gateway; remoteItActive=true; serves Watteco Clim'o temp sensors
6770 | Device 70B3D5E75F200626 | ceacd850-b97d-11f0-bb17-9fd297bb4ff9 | boiler-control | lorawan-sensor | Watteco | fw 3.5.2 | Yes | No | — | N/A | none | N/A | PROVEN | Clim'o; label=gk-6770-tempsensor-1; linked-output-num=2; current 19.6°C (from decoded JSON)
6770 | Device 70B3D5E75F2006BB | 5e954e70-b979-11f0-bb17-9fd297bb4ff9 | boiler-control | lorawan-sensor | Watteco | fw 3.5.2 | Yes | No | — | N/A | none | N/A | PROVEN | Clim'o; label=gk-6770-tempsensor-2; linked-output-num=3; current 22.4°C (from decoded JSON)
6770 | gk-6770-maindb-r10a | 3f486dc0-a904-11f0-aef9-63eb6f282fc9 | R10A Modbus Gateway | remoteit | — | — | Unknown | No | — | N/A | none | N/A | PROVEN | R10A IoT Gateway; modbus metering
6770 | gk-6770-boiler-r10a | 886deb70-efcb-11f0-8fe3-c5f1d9f73790 | R10A Modbus Gateway | remoteit | — | — | Unknown | No | — | N/A | none | N/A | PROVEN | R10A IoT Gateway
6770 | gk-6770-ElecAMR-1 | 38841781-cec7-11f0-bef1-9775690abcb2 | AMR_profile | amr | — | — | Unknown | No | — | N/A | none | N/A | PROVEN | No schedule
6770 | gk-6770-GasAMR-1 | 37151e30-cec7-11f0-bef1-9775690abcb2 | AMR_profile | amr | — | — | Unknown | No | — | N/A | none | N/A | PROVEN | No schedule
6770 | gk-6770-various-tuya/meter | (various) | tuya/meterOnly | other | Tuya/— | — | Yes/No | No | — | N/A | none | N/A | PROVEN | ~12 Tuya + 7 meterOnly sub-boards + cellar/fridge/freezer; 41 total devices at site

## By Device Type
DeviceType | SitesSeen | TotalDevices | ScheduleInTB | ScheduleFormat | ScheduleKeys | DisplayFeasibility | Notes
boilerControl-V2 | 6261, 6097, 6164, 122 | 4 | Yes | boilerControl-json ({schedule:[{time,loops,value}]}) | CHZ1.schedule, CHZ2.schedule, DHW.schedule, recirc_pump.schedule, accom_1.schedule, accom_2.schedule (SHARED_SCOPE authoritative; CLIENT_SCOPE copy) | Feasible-now | Fully handled by existing schedule.js decoder. loops 7-char string Mon=pos0..Sun=pos6. V3 key naming (channel.schedule). 4 active schedule channels typical; accom_1/accom_2 usually empty. Some sites have weekday/weekend split (multi-entry loops). recirc_pump uses 1000/-1000 not temperature.
boilerControl-V1 | 6769, 4331, 6770 | 3 | Yes | boilerControl-json ({schedule:[{time,loops,value}]}) | output2Schedule, output3Schedule, output4Schedule (CLIENT_SCOPE + SHARED_SCOPE; outputs[].schedules embedded array is authoritative) | Feasible-now | Same JSON format as V2 but different key names (outputNSchedule not channel.schedule). output2=CH zone1, output3=CH zone2, output4=DHW. DHW only active if output1OutputMask[3]=true. CLIENT top-level key can be stale vs outputs[].schedules embedded (DEDUCED from site 4331 finding). CAUTION: override flag (outputNOverride=1) means schedule is superseded.
salus-IT700 | 6261, 6097, 6164, 122, 6769, 4331, 6770 | 7+ thermostats | No | flag-only (scheduleEnable integer: 0=off 1=on 2=hold) | scheduleEnable (TIMESERIES only) | Not-feasible | IT700TX thermostat stores schedule ON-DEVICE only. Not accessible via TB. Only scheduleEnable flag is visible. To show IT700 schedules, would need Salus cloud API — not currently in scope. scheduleEnable=2 (hold/override) observed at 6164 and 122.
salus-IT700-gateway | 6261, 6097, 6164, 122, 6769, 4331, 6770 | 7+ gateways | No | none | — | Not-feasible | SAWZ600GW ZigBee gateway for IT700TX. ALL gateways observed show active=false (offline) across all sites. Thermostats remain active independently. UNRESOLVED: whether this is a persistent issue or expected state.
salus-IT500 | 5208 | 6 | Partial | nibble-encoded (A00-A06 keys, 24-char ASCII-offset strings in SERVER_SCOPE) | SERVER_SCOPE.schedule (A00-A06 day keys), SERVER_SCOPE.programs (C00-C06, empty) | Feasible-pending-Spencer | Schedule IS stored in TB but encoding is proprietary Salus format. Decoding blocked pending Spencer/bridge code clarification (Q1). All 6 IT500 at site 5208 are OFFLINE. vendor_id=salus-it500. programs key exists but C00-C06 all empty (purpose UNRESOLVED).
tuya-owon | 6261, 6097, 6164, 4331, 6769 | 25+ | Partial | Base64 binary (5 bytes/record) in TIMESERIES.schedule; and/or scheduleHEX hex-string in SERVER_SCOPE | TIMESERIES.schedule (Base64 binary blob); SERVER_SCOPE.scheduleHEX (hex-string for some devices) | Feasible-pending-Spencer | Two formats: (1) TIMESERIES.schedule = 5B/record Base64 binary blob. Byte0=day-bitmask (bit0=Sun..bit6=Sat), Byte1=hour, Byte2=minute, Byte3=action (0=preheat/1=service? — DEDUCED), Byte4=enabled. Decoder needed. (2) SERVER_SCOPE.scheduleHEX = raw hex-string, Tuya DPS spec needed. Action byte semantics UNRESOLVED (Q3).
tuya-tongou | 6261, 6097, 6164, 4331, 5208, 122, 6769, 6770 | 50+ | Partial | scheduleHEX comma-delimited string in SERVER_SCOPE (devId,loops,time,action tuples) — some devices; light_mode=relay others have no schedule | SERVER_SCOPE.scheduleHEX (comma-delimited, tongou devices with schedule only) | Feasible-now | scheduleHEX comma-delimited format: 'devId,7charLoops,HH:MM,on¦off,...' uses same 7-char loops string as boilerControl. PROVEN decodeable (site 4331 examples). Some tongou devices have light_mode=relay (simple on/off, no schedule). Only a subset of tongou devices have scheduleHEX populated.
intesis | 6770 | 3 | No | none | — | Not-feasible | Thin TB wrapper for Intesis HVAC units. All schedule and configuration lives in Intesis hardware/cloud, not in TB. Only live operational telemetry available: isOnline, mode, currentTemperature, heatingActive, setPoint, connectivity. Control path (write back) UNRESOLVED.
lorawan-sensor | 6769, 6770 | 5 (122 planned but not yet in TB) | No | none | — | Not-feasible | Watteco Clim'o LoRaWAN temperature+humidity sensors. No schedule. Current temp in decoded JSON field (NOT top-level temperature field which is always 269.8). linked-output-num CLIENT_SCOPE attr links to boilerControl output. V1 linkage stored on sensor; V3 linkage stored on boilercontrol. Site 122 has provisioned sensors but no lwgateway deployed — data not flowing.
lorawan-gateway | 6769, 6770, 4331 | 3 (4331 inactive) | No | none | — | Not-feasible | lwgateway devices (remoteItProfile); serve Watteco Clim'o sensors. 4331 gateway inactive (alarm: Remote.IT Gateway Offline). No schedule. remoteItActive telemetry key.
amr | 6261, 6097, 6164, 122, 6769, 4331, 6770 | 14+ | No | none | — | Not-feasible | AMR_profile devices (ElecAMR, GasAMR). No schedule. Most show active=false (inactive) across all sites. consumption_wh telemetry key only. Site 6261 GasAMR has siteName='#REF!' provisioning error.
remoteit | 6261, 6769, 4331, 6770 | 6+ | No | none | — | Not-feasible | remoteItProfile (R10A Modbus gateways and remote.it VPN devices). No schedule. Metering sub-boards accessed via R10A Modbus. Site 6261 kitchen-r10a and maindb-r10a both inactive.
other | 4331, 6770 | 10+ | No | none | — | Not-feasible | meterOnly sub-distribution boards (meterOnlyProfile). Tracks electrical power/energy per circuit. No schedule. Part of metering_map on R10A gateway.

## Spencer Questions
QRef | Question | Blocker | Category | Status
Q1 | What is the encoding for SERVER_SCOPE.schedule A00-A06 values on Salus IT500 devices? Example from gk-5208-salusit500-f1: all 7 days = '00>570F0;0?0=0>0@DE0E0>0' (24 chars). Appears to use ASCII-offset nibbles but pattern unclear. Spencer or the legacy Salus bridge code (services/tb-device.js) should hold the decoder. | Yes | format | UNRESOLVED
Q2 | Are the time values in boilerControl schedule JSON (e.g. '09:00', '23:00') in Europe/London local time or UTC? Both V1 (output2Schedule) and V3 (CHZ1.schedule) use HH:MM strings. The OOH dashboard must display schedules in the correct local time for the site. DEDUCED to be Europe/London local time based on observed patterns (06:00 DHW on, typical pub trading hours) but this needs explicit confirmation before the display feature ships. | Yes | timezone | DEDUCED needs confirmation
Q3 | What is the exact semantics of byte 3 (action byte) in the Tuya TIMESERIES.schedule Base64 binary blob? 5-byte records: byte3 observed values are 0x00 and 0x01 only. Pattern across fryers/grills suggests 0x00=preheat/warm-up phase (earlier times) and 0x01=full service temperature on (latest time). Could alternatively be 0=off / 1=on. Affects how timetables are described to operators (e.g. 'preheat 09:15, full service 11:15' vs 'off until 11:15'). | No | format | UNRESOLVED
Q4 | Why do ALL Salus SAWZ600GW gateways show active=false (offline) across every site surveyed (6261, 6097, 6164, 122, 6769, 4331, 6770) while the paired IT700TX thermostats show active=true and have recent lastActivityTime timestamps? Is this a known/expected state, a systemic connectivity issue, or a stale active flag? The IT700TX thermostats appear to operate independently of the gateway once paired. Understanding this matters for OOH dashboard health reporting. | No | authority | UNRESOLVED
Q5 | For boilerControl V1 (app 2.8.x), which is the authoritative running schedule: (a) the top-level outputNSchedule key in CLIENT_SCOPE, or (b) the embedded outputs[N].schedules array in CLIENT_SCOPE? Site 4331 shows a clear divergence: top-level output2Schedule shows 11:00=20°C / 22:00=15°C but outputs[1].schedules shows 11:00=21°C / 12:00=15°C / 17:00=15°C / 18:30=15°C. The SHARED_SCOPE matches the embedded outputs[] value, suggesting outputs[] is what the device actually reads. DEDUCED but needs confirmation before the dashboard uses either source. | Yes | authority | DEDUCED needs confirmation
Q6 | Can the IT700TX thermostat's schedule body be retrieved from the Salus cloud API (not ThingsBoard)? The IT700TX stores its schedule on-device only; TB only exposes scheduleEnable (0/1/2 flag). If a Salus cloud API endpoint exists that returns the full weekly schedule for a device identified by its eUID or salusSerialNumber, the OOH dashboard could fetch and display IT700 schedules. If no such API exists, IT700 schedule display is Not-feasible. | No | format | UNRESOLVED
Q7 | Site 122 has two Watteco Clim'o LoRaWAN sensors provisioned in the LNS (EUIs 70B3D5E75F2004DD and 70B3D5E75F2001DA, both provisioned=true in boilercontrol CHZ1.lorawan_devices) but NO lwgateway device exists at site 122 in ThingsBoard — TB search returns zero results for both EUIs and for 'gk-122-tempsensor'. Without the gateway, CHZ1 at site 122 operates without temperature feedback. What is the deployment timeline for the lwgateway at site 122, and is this a known open action? | No | deployment | UNRESOLVED